## Coug Lab
Quantity | Existing or Wish List Item | Equipment Name | Equipment Footprint (WxDxH) | Equipment Clearance Size/Description | Power Requirements | Ventilation Requirements | Plumbing Requirements | Air supply | Operational Restrictions | Notes
Existing items we teach with in ETRL-24
1 | Haas Mini Mill (vertical machining center) | West MM1 | Please see attached document Minimill…..pdf | 24" behind for cabinet opening | 208V 3 phase 40 amps | Yes | Yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Haas Mini Mill (vertical machining center) | East MM1 | Please see attached document Minimill…..pdf | 24" behind for cabinet opening | 208V 3 phase 40 amps | Yes | Yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Haas TL-1 toolroom lathe | North TL | Please see attached document TL-1…..pdf | 24" behind for cabinet opening | 208V 3 phase 40 amps | Yes | Yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Haas TL-1 toolroom lathe | South TL | Please see attached document TL-1…..pdf | 24" behind for cabinet opening | 208V 3 phase 40 amps | Yes | Yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Haas VF-1SS VMC | HMFIC | Please see attached documentVF2-ss…..pdf | 24" behind for cabinet opening | 208V 3 phase 70 amps | Yes | Yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Bridgeport series 1 Mill | BP | 80" X 72" x 96" | 24" on each end of machine X-Axis | 208V 3 phase 30amps | Yes | NO | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Cold saw | Cold saw | 72" X 48" X 96" | 72" left and right | 208V 3 phase 20 amps | yes | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Horizontal band saw | Baileigh | 24"x 72"X36" | 96" left and right | 110V 15 amps | no | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Monarch EE toolroom lathe | EE | 96" X 48"X 60" | 60" left, 36" front and back | 208V 3 phase 20 amps | yes | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Rayjet 80 watt CO2 laser | Ray | 48" X 32" X 36" | 36" front | 110V 15 amps | YES (ventilation is critical) | Yes | NO | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Fanuc Lrmate 200IC | Robotic trainer | 72"x36"X 72"
1 | Fein Belt sander | Belt sander | 24"x 72"X36" | 36" front, sides | 110V 15 amps | yes | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Raised3d pro | Pro | 24"x24"x36" | NO | 110V 15 amps | no | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Raised3d XL | XL | 24"x24"x24" | No | 110V 15 amps | no | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
4 | Prusa MK3 printers | Prusa | 16"x16"x16" | No | 110V 15 amps | no | NO | no | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE) | This equipment is industrial machine tools please see operational restrictions
1 | Browne and Sharp CMM | B&S | 72"x36"X96" | 36"front | 110V 15 amps | no | NO | yes
7 | Haas CNC simulators | sims | 24"x24"x24" | 24" front | 110V 15 amps | no | NO | no
6 | CAM training stations |  | 72" X 48" X 36" | 36" front | 110V 15 amps | no | NO | no
1 | Material storage rack | Pallet rack | 144"x36"x192" | 72" left and right |  | no | NO | no
4 | Lista cabinets (400lb drawers) | storage | 36"x36"x48" | 24" front
5 | Lista workstation benches | workspace/storage | 72"x36"x36 | 24" front, left and right
Wish list items
1 | Haas UMC 750 | Universal machining center | 120" x 120" X 96" | 36" front, sides and back | 208v 3 phase 80amps | yes | yes | Compressed air 8CFM @ 100PSI(dry) | Only to be used by students either taking or having taken ME 312, Cougarshop employee's (at this time no faculty are qualified -NONE)
1 | Haas SL-20 with live tooling | CNC lathe | 120"x60"x72" | 36" left and front | 208v 3 phase 60amps | yes | yes | Compressed air 8CFM @ 100PSI(dry)
1 | Renishaw equator 500 | CMM | 72"x72"x72" | 24" front | 110v 15 amps | no | no | Compressed air 8CFM @ 100PSI(dry)
1 | Thermal toolsetting machine | Haimer 560-200 | 36"x36" | 24" left, right, front | 208v 3 phase 20amps | no | no | Compressed air 8CFM @ 100PSI(dry)
1 | Fanuc Rb-30ia Robotic workstation | Cobot | 72"x72"x72" | 24" front | 110v 15 amps | no | no | Compressed air 8CFM @ 100PSI(dry)

## Fab Lab
Qty | Existing/Wish | Equip. Name | Footprint | Clearance | Voltage | Phase | Amps | CFM Req'd | Duct dia. (inch) | Notes
1 | Existing | Rockwell 8" joiner | 66" X 16" | 15'-0" min. infeed & outfeed | 208/240 | 1 | 6 | 400 | 4"
1 | Existing | Powermatic 20" Planer | 48" X 36" | 15'-0" min. infeed & outfeed | 208/240 | 3 | 15 | 500 | 5"
1 | Existing | SawStop 10" cabinet saw | 68" X 86" | 15'-0" min. infeed & outfeed | 208/240 | 1 | 13 | 350 | 4-­‐5"
1 | Existing | SawStop 10" cabinet saw | 72" X 86" | 15'-0" min. infeed & outfeed | 208/240 | 1 | 13 | 350 | 4-­‐5"
1 | Existing | Festool Miter Saw + workstation | 24" x 120" | 15'-0" min. infeed & outfeed | 120 | 1 | 15 | 350 | 4"
1 | Existing | Porter-Cable 3 Hp Router + Table | 32" X 24" | 15'-0" min. infeed & outfeed | 120 | 1 | 15 | 350 | 3-­‐4"
1 | Existing | ShopBot 96" X 48" CNC | 120" X 79" | 9'-0" min. infeed & outfeed | 208/240 | 3 | 15 | 350 | 4" | Compressed air req'd
1 | Existing | ShopBot 24" x 36" DesktopMax | 48" x 36" | 3'-0" x 3'-0" for operator | 120 | 1 | 15 | 350 | 3-4" | Compressed air req'd
1 | Existing | ShopBot 5-Axis mill | 96" x 96" | 9'-0" min. infeed & outfeed | 208/240 | 3 | 3 | NA | NA | Compressed air req'd
1 | Existing | DoAll Band Saw | 36" X 62" | 3'-0" x 6'-0" for operator | 208/240 | 3 | 24 | 550 | 5" | Starting amps. Running amps = 3.
1 | Existing | Powermatic Model 81 bandsaw | 32" X 48" | 3'-0" x 4'-0" for operator | 208/240 | 1 | 6.6 | 550 | 5"
1 | Existing | Powermatic Drill Press | 24" x 36" | 3'-0" x 3'-0" for operator | 120 | 1 | 8 | NA | NA
1 | Existing | "Max" spindle sander | 24" X 24" | 3'-0" x 3'-0" for operator | 208/240 | 3 | 6 | 350 | 4"
1 | Existing | Powermatic edge sander | 54" X 20" | 5'-0" x 3'-0" for operator | 208/240 | 1 | 10 | 550 | 5"
1 | Existing | Powermatic Combination Sander | 24" X 24" | 3'-0" x 3'-0" for operator | 208/240 | 3 | 6 | 400 | 4-­‐5"
1 | Existing | TimeSaver 43" Wide Belt Sander | 62" x 52" | 15'-0" min. infeed & outfeed | 208/240 | 3 | 68 | 1000 | 5" | Compressed air req'd
1 | Existing | Oneida Cyclone 5 HP blower | 60"x 36" | 3'-0" x 3'-0" min. service | 208/240 | 3 | 12 | 2150 | 8" | Air moved at 2" static pressure
2 | Existing | Penn State Industries 2HP Blower | 15" X 9" | 2'-0" x 2'-0" min service | 208/240 | 1 | 8 | 1350 | 6" | Air moved at adequate static pressure
1 | Existing | 10HP 80 Gal. Air Compressor | 41" X 31" | 4'-0" x 3'-0" min. service | 208/240 | 3 | 22 | 14 SCFM @90 PSI | NA | Compressed air delivery
1 | Existing | Universal Laser Systems ILS9.150D | 57" X 44" | 6'-0" x 3'-0" min. operator | 208/240 | 1 | 10 | 700 | (2) 4" | Compressed air req'd
1 | Existing | Universal Laser Systems X-­‐660 | 44" X 36" | 4'-0" x 3'-0" min. operator | 120 | 1 | 10 | 500 | (2) 4" | Compressed air req'd
1 | Existing | Full Spectrum 90 Watt Laser | 48" x 36" | 4'-0" x 3'-0" min. operator | 208/240 | 1 | 10 | 500 | (2) 4" | Compressed air req'd
1 | Existing | SafetySpeed Panel Saw | 96" x 24" | 8'-0" x 3'-0" min. operator | 120 | 1 | 15 | 350 | 3-4"
1 | Existing | Digital Knife Cutter | 144" x 72" | 3'-0" min. all around for operator | 120 | 1 | 15 | NA | NA | Compressed air req'd
1 | Existing | 3D Printer Array | 144" x 24" | 12'-0" x 3'-0" for operator | 120 | 1 | 15 | NA | NA | Footprint and clearance is total for all printers. Can be reconfigured if necessary.

## FIZ
I will try to answer this to the best of my abilities. The overall foot[print of each machine that I will be writing in is an estimate but I am adding in its operational footprint for materials and operator as well. For instance, a mitre saw takes up a 2’x2’ table space but ours has a footprint of 4’x20’ because of 10’ of material length in either direction and a place for the operator to stand. Machines that do not have an operational footprint included are fairly small risk and only require space for an operator. • Equipment Name • If it is existing equipment we have or if it is a wish list item • Quantity (if we have more then 1) • Equipment Footprint • Equipment Clearance Requirements • Power Requirements • Ventilation Requirements • Plumbing Requirements • Operational Restrictions • Mis. Notes and Comments. Metal Studio (Current machines): Horizontal bandsaw – 2’x4’ footprint – 4’x20’ operational footprint Colt cut saw – 2’x2’ footprint – 4’x20’ operational footprint Drill Press – 2’x2’ footprint – 4’x4’ operational footprint Tormach mill – 6’x6’ footprint – 8’x10’ operational footprint Combination sander – 2’x3’ footprint – 4’x4’ operational footprint Bench grinder – 2’x2’ footprint – 4’x4’ operational footprint Heavy duty shear – 6’x6’ footprint – 6’x12’ operational footprint Electrical Fabrication Studio (Current machines) Soldering iron Power Supply Voltera all in one PCB station Oscilloscope Othermill All machines fit on a 3’x16’ desk Wood Studio (Current Machines) Combination sliding mitre saw – 2’x’2 – 4’x20’ operational footprint Bandsaw – 3’x3’ – 4’x6’ operational footprint CNC router – 6’x6’ – 8’x10’ operational footprint Drill Press – 2’x2’ – 4’x4’ operational footprint Panel saw – 5’x10’ – 5’x10’ operational footprint Dust collector– 6’x3’ Scroll saw – 2’x3’ Welding Studio (Current machines) 3x Mig welders – 2’x3’ TIG welder – 2’x3’ CNC plasma – 8’x8’ Sand blaster – 4’x4’ Air compressor – 3’x3’ Misc Equipment: Waterjet – 4’x4’ CNC Foam cutter – 6’x6’ 10x 3d Printers – 2’x3’ each Trotec Laser – 4’x3’ Thunder Laser – 6’x7’ Wishlist: Heavy duty brake (Est. $15,000) Shop air system Larger dust collection system Larger fume extraction system (our own fan and vent to the roof) Overhead crane (Or portable shop crane) Table saw (Est. $4,000) Large Planar (Est. $7,000) Large belt sander(Est. $20,000) Jointer (Est. $4,000) Large bandsaw (Est. $5,000) Larger Avid CNC router (Est. $26,000) Lathe (Est. $6,000) Laser welder (Est. $18,000) Larger waterjet CNC metal laser (Est. $280,000) Metal 3D printer (Est. $300,000) All machines have a power requirement of either single phase or 3 phase. Preferably the FIZ will have overhead bus bars that will allow us to have modularity with where we route power. The shop would need 120 20 amp, 230-250 VAC single phase, 220-240VAC 3 phase, and a large main switch for emergency shutoff of all machines. The shop would need large bay doors or roll up doors minimum 10ft preferably 12ft tall and 10ft wide. The shop floor needs to be open with moveable partitions. Having segregated rooms is a safety hazard because there is no line of sight for the machines and closed doors mute sound so we cannot hear if someone is in danger. The FIZ would require its own vent stack to the roof because of our lasers, welders, and possibly other projects that clubs can bring in. Canopy hoods would also be great. There needs to be plumbing and routing for cold water, shop air, dust collection, and fume extraction. The FIZ also needs a storage area.